## standard
Inlet RH conversions |  | Pressure | 1013 | hPa | [12 empty] | Dewcon raw |  | AH Normalized |  | Hum ratio | grams water /g dry air | specific humidity | grams water/kg moist air
| Cv=1-(0.0001*(SQRT((0.1*T)+1)+4)) | Temperature (C) | 2 | C | 0.99949 | Cv | 7.0584 | Ps | 5.5613 | fs
| %RH=(f/fs)*100=(Pd/Ps)*100 | Relative Humidity | 20 | %RH | 1.1123 | g/m3 | 1.4117 | Pd | 0.13951 | %vol | 0.86797 | g/kg |  |  | -18.4959 | DP | 1.1204 | g/m3 corrected to 0 | 1.1204 | g/Nm3 | 0.00086797 | kg/kg | 0.86722 | g/kg
19920
Outlet Moisture Conversions -1 (equations based on Temperature in C) For Air ONLY
Ps=6.1078*EXP(17.08085*T/(234.175+T))
| Pm | Pressure at measuring point, hPa | 1013 | hPa
| Cv=1-(0.0001*(SQRT((0.1*T)+1)+4)) | Gas/Probe Temperature (C) | 113.1 | C | 0.99925 | Cv | 1591.4999 | Ps | 893.4767 | fs
| g/m3 | Absolute Moisture | 148.4 | g/m3 |  |  | 264.3366 | Pd | 26.1311 | %vol | 219.6075 | g/kg | 16.6093 | %RH | 66.2719 | DP | 209.8507 | g/m3 corrected to 0 | 209.8507 | g/Nm3 | 0.21961 | kg/kg | 180.0641 | g/kg
| %vol=0.124522(f) = Pd/Pa | % Volume | 15 | %vol | 85.1893 | g/m3 | 151.7429 | Pd |  | %vol | 109.5852 | g/kg | 9.5346 | %RH |  |  | 120.4626 |  | 120.4626 | g/Nm3
| GKG=621.98*[Pd/(Pm-Pd)], | Humidity Ratio | 839.9 | g/kg | 582.0031 | Pd | 326.7397 | g/m3 | 57.5341 | %vol |  |  | 36.5695 | %RH | 85.2059 | DP | 462.0389 |  | 462.0389 | g/Nm3
| Pd=Cv*461.51*(T+273.15)*D13*0.00001 | Partial Pressure H2O |  | Pd (Pa)
| DP=[234.175*LN(Pd/6.1078)]/[17.08085-LN(Pd/6.1078)] | DewPoint |  | DP (C)
[6 empty] | 9.1667 | 272.6281 | 25
Outlet Moisture Conversions -2 (equations based on Temperature in C) For Air ONLY
Ps=6.1078*EXP(17.08085*T/(234.175+T))
| Pm | Pressure at measuring point, hPa | 1013 | hPa
| Cv=1-(0.0001*(SQRT((0.1*T)+1)+4)) | Gas/Probe Temperature (C) | 120 | C | 0.99924 | Cv | 1991.8604 | Ps | 1098.6261 | fs
| g/Nm3 | Absolute Moisture | 300 | g/m3 |  |  | 543.914 | Pd | 53.7694 | %vol | 721.1974 | g/kg | 27.3068 | %RH | 83.4892 | DP | 431.8054 | g/m3 corrected to 0 | 431.8054 | g/Nm3
| %vol=0.124522(f) = Pd/Pa | % Volume | 100 | %vol | 557.961 | g/m3 | 1011.6092 | Pd |  | %vol | 452407.8223 | g/kg | 50.7872 | %RH |  |  | 803.0838 |  | 803.0838 | g/Nm3
| GKG=621.98*[Pd/(Pm-Pd)], | Humidity Ratio | 266.1 | g/kg | 303.5304 | Pd | 167.4146 | g/m3 | 30.0059 | %vol |  |  | 15.2385 | %RH | 69.4248 | DP | 240.9684 |  | 240.9684 | g/Nm3
| Pd=Cv*461.51*(T+273.15)*D13*0.00001 | Partial Pressure H2O |  | Pd (Pa)
| DP=[234.175*LN(Pd/6.1078)]/[17.08085-LN(Pd/6.1078)] | DewPoint |  | DP (C)
|  | Gas Density dry air | 0.89751 | kg/m3
|  | Mol wt mix air/h2o | 18.106 | kg/kmol
|  | Gas Density Mix | 0.56113 | kg/m3
[6 empty] | 9.1667 | 272.6281 | 25
| Molecular Wt of Water= | 18.106 | kg/kmol
| Molecular Wt of air= | 28.96 | kg/kmol
| Universal Gas Constant | 8.314 | J/kmol
| Gas Constant of Air= | 0.28709 | kJ/(kg K)
| Gas Constant of Water= | 0.45918 | kJ/(kg K)
Note: g/Nm3 is normalized to temperature (0C) and pressure (1013 hPa). The actual units of the H2O Sensor are only corrected to temperature because we do not have a pressure measurement.
|  |  | 248 | DPF | 107.2222 | C
|  |  | 120 | DPC | 225 | F

## wetbulb
% volume | Temperature C | Pressure (HPa) | absolute humidity at process g/m3 | vapor pressure Hpa | saturation pressure Hpa | rh decimal | dewpoint temperature C | Rh % | Wet Bulb Temperature C | A | K | P | Main eq | Tw | Solver |  | wet bulb equation
8.5 | 89 | 1013 | 51.4794 | 85.9791 | 674.1861 | 0.12753 | 42.8977 | 12.753 | 49.6535 | 159960000 | 0.000662 | 1013 | -28261562.2779 | 82.025 | 131698437.7221 |  | 0=((Tw*K*P)-(K*T*P)-Pw)*EXP(3999.91/(Tw+234.175))+1.5996*10^8
7.9 | 85 | 1013 | 48.3802 | 79.9109 | 577.3189 | 0.13842 | 41.5 | 13.8417 | 48.2293 | 159960000 | 0.000662 | 1013 | -25847788.3133 | 81.7714 | 134112211.6867 |  | -3814801502.2584
15.86 | 93.88 | 1013 | 94.7769 | 160.4248 | 810.4742 | 0.19794 | 55.4092 | 19.7939 | 59.1801 | 159960000 | 0.000662 | 1013 | -159960000 | 58.3421 | 0
10 | 155 | 1013 | 51.2247 | 101.1362 | 5499.9837 | 0.018388 | 46.0494 | 1.8388 | 66.6171 | 159960000 | 0.000662 | 1013 | -159960000 | 56.295 | -6.5565e-07 |  | T is temp C
10 | 155 | 1013 | 51.2247 | 101.1362 | 5499.9837 | 0.018388 | 46.0494 | 1.8388 | 66.6171 | 159960000 | 0.000662 | 1013 | -159960000 | 56.295 | -8.0466e-06 |  | D2 is gas vapor pressure
[10 empty] | 159960000 |  | 1013 | 0 |  | 159960000 |  | .000662 is pschometric constant - K
[10 empty] | 159960000 |  | 1013 | 0 |  | 159960000 |  | P - total pressure used 1013 for 1 atm. Is a vairable input if total pressure varies
Tw is wet bulb
[16 empty] | A | 159960000 | B | 0
[16 empty] | K | 0.000662
[16 empty] | P | 1013
[16 empty] | T | 85
Pw
Tw

## Peet WB
% volume | Temperature C | Pressure (HPa) | absolute humidity at process g/m3 | Normal Abs Humidity g/Nm3 | vapor pressure Hpa | saturation pressure Hpa | rh decimal | dewpoint temperature C | Rh % | Factor 1 | Factor 2 | Factor 3 | Factor 4 | Factor 5 | Factor 6 | Factor 7 | Factor 8 | Factor 9 | Factor 10 | Factor 11 | Wet Bulb Temperature C | humidity ratio g/kg | A | K | P | Main eq | Tw | Solver | wet bulb equation
59.3 | 110.3 | 1013 | 339.1872 | 476.1635 | 599.7977 | 1449.263 | 0.41386 | 85.9758 | 41.3864 | 0.36723 | 0.85343 | -0.031179 | 2.3422 | 86.3155 | 60.7758 | 0.36859 | -0.32684 | 2.3667 | 86.3142 | 60.7763 | 86.3142 | 902.856 | 159960000 | 0.000662 | 1013 | -128098967.4764 | 92.3004 | 31861032.5236 | 0=((Tw*K*P)-(K*T*P)-Pw)*EXP(3999.91/(Tw+234.175))+1.5996*10^8
85 | 89 | 803.21 | 408.1817 | 682.5414 | 681.7304 | 674.1861 | 1.0112 | 89.2908 | 101.119 | 0.4078 | -8.8201 | 0.0043651 | 3.1667 | 95.5067 | 86.0737 | 0.40784 | -0.46932 | 3.1676 | 95.5069 | 86.0736 | 95.5069 | 3490.4857 | 159960000 | 0.000662 | 1013 | -335177343.5464 | 71.3514 | -175217343.5464 | -17645392216.3462
29.8781 | 96.9077 | 1070.381 | 187.1162 | 239.916 | 319.3348 | 906.0751 | 0.35244 | 70.599 | 35.2437 | 0.29611 | 0.2311 | -0.057079 | 1.3132 | 70.4909 | 31.7531 | 0.30092 | -0.16379 | 1.3685 | 70.47 | 31.7565 | 70.47 | 264.4576 | 159960000 | 0.000662 | 1013 | -159959909.7788 | 71.8601 | 90.2212
29.9707 | 97.3248 | 1065.9113 | 186.7022 | 240.6599 | 318.9872 | 919.9535 | 0.34674 | 70.5737 | 34.6743 | 0.29642 | 0.23346 | -0.056681 | 1.3166 | 70.566 | 31.8558 | 0.30124 | -0.1643 | 1.3723 | 70.545 | 31.8592 | 70.545 | 265.6276 | 159960000 | 0.000662 | 1013 | -159959937.4812 | 71.8516 | 62.5188 | T is temp C
33.1335 | 97.2034 | 1023.9644 | 198.347 | 266.0564 | 338.7717 | 915.8962 | 0.36988 | 71.9773 | 36.988 | 0.30637 | 0.28582 | -0.051299 | 1.4335 | 72.623 | 34.8016 | 0.31007 | -0.18196 | 1.479 | 72.611 | 34.8038 | 72.611 | 307.5181 | 159960000 | 0.000662 | 1013 | -350363016.3755 | 56.295 | -190403016.3755 | D2 is gas vapor pressure
[22 empty] | #DIV/0! |  |  | .000662 is pschometric constant - K
|  |  |  | Mol wt ratio M | [17 empty] | #DIV/0! |  |  | P - total pressure used 1013 for 1 atm. Is a vairable input if total pressure varies
|  |  |  | 1.06 | [17 empty] | #DIV/0! |  |  | Tw is wet bulb
|  |  |  | 1.06 | [17 empty] | #DIV/0!
|  |  |  | 1.06 | [17 empty] | #DIV/0! |  | A | 159960000 | B | 90.2212
|  |  |  | 1.06 | [17 empty] | #DIV/0! |  | K | 0.000662
|  |  |  | 1.06 | [17 empty] | #DIV/0! |  | P | 1013
|  |  |  | 1.06 | [17 empty] | #DIV/0! |  | T | 200
|  |  |  | 1.06 | [17 empty] | #DIV/0! |  | Pw
[22 empty] | #DIV/0! |  | Tw

## spray dry sens
% volume | Temperature C | Temperature F | absolute humidity at process | vapor pressure | saturation pressure | rh decimal | dewpoint temperature | Rh | Wet Bulb Temperature | A | K | P | Main eq | Tw | Solver |  | wet bulb equation
7 | 50 | 122 | 47.5137 | 70.8148 | 123.3353 | 0.57417 | 39.223 | 57.4165 | 41.3504 | 159960000 | 0.000662 | 1013 | -159960064.8173 | 40.7938 | -64.8173 |  | 0=((Tw*K*P)-(K*T*P)-Pw)*EXP(3999.91/(Tw+234.175))+1.5996*10^8
7.2 | 49.5 | 121.1 | 48.947 | 72.8382 | 120.3131 | 0.60541 | 39.7505 | 60.5406 | 41.6431 | 159960000 | 0.000662 | 1013 | -32941437.9995 | 68.5166 | 127018562.0005 |  | -2732716962.9218
7.4 | 49 | 120.2 | 50.3848 | 74.8616 | 117.3547 | 0.63791 | 40.2655 | 63.7909 | 41.933 | 159960000 | 0.000662 | 1013 | -22435172.0364 | 76.1548 | 137524827.9636
6.8 | 50.5 | 122.9 | 46.0848 | 68.7914 | 126.4224 | 0.54414 | 38.6824 | 54.4139 | 41.0537 | 159960000 | 0.000662 | 1013 | -41157625.1651 | 63.4968 | 118802374.8349 |  | T is temp C
6.6 | 51 | 123.8 | 44.6604 | 66.768 | 129.5756 | 0.51528 | 38.1278 | 51.5283 | 40.7522 | 159960000 | 0.000662 | 1013 | -31860072.3653 | 67.5388 | 128099927.6347 |  | D2 is gas vapor pressure
27.1589 | 98.2012 | 208.7622 | 160.4083 | 274.711 | 949.6916 | 0.28926 | 67.1432 | 28.9263 | 69.1335 | 159960000 | 0.000662 | 1013 | -159960000 | 68.7283 | 0 |  | .000662 is pschometric constant - K
27.5923 | 84.2381 | 183.6286 | 169.3377 | 279.105 | 560.2646 | 0.49817 | 67.5038 | 49.8166 | 68.8488 | 159960000 | 0.000662 | 1013 | -159952422.412 | 68.359 | 7577.588 |  | P - total pressure used 1013 for 1 atm. Is a vairable input if total pressure varies
28.423 | 84.3439 | 183.8191 | 174.3842 | 287.5078 | 562.6073 | 0.51103 | 68.1803 | 51.1028 | 69.4593 | 159960000 | 0.000662 | 1013 | -9010908025.9068 |  | -8850948025.9068 |  | Tw is wet bulb
28.3657 | 86.385 | 187.493 | 173.0444 | 286.9268 | 609.4401 | 0.4708 | 68.134 | 47.0804 | 69.5307 | 159960000 | 0.000662 | 1013 | -9031538270.39 |  | -8871578270.39
28.4283 | 88.3462 | 191.0231 | 172.4848 | 287.5581 | 657.4802 | 0.43736 | 68.1843 | 43.7364 | 69.6746 | 159960000 | 0.000662 | 1013 | -9082514388.8969 |  | -8922554388.8969 | A | 159960000 | B | 137524827.9636
28.5017 | 89.08 | 192.344 | 172.58 | 288.3006 | 676.2549 | 0.42632 | 68.2432 | 42.6319 | 69.7619 | 159960000 | 0.000662 | 1013 | -9114846880.6678 |  | -8954886880.6678 | K | 0.000662
[16 empty] | P | 1013
[16 empty] | T | 49.5
Pw
Tw

## SQ BTU Calcs
Boiler Size (lb/hr) | Steam Temperature (F) | Steam Pressure (psia) | Vapor Enthalpy (BTU/lb) | Liquid Enthalpy (BTU / Lb) | Steam Quality (decimal) | Steam Enthalpy (Btu/hr) | Yearly Operation (Hrs) | BTUs / yr | Difference in BTUs | natural gas volume (mcf) | Boiler efficiency (decimal) | Gas price / mcf | Yearly Gas Bill $ | NCG Heat tranfer hit (decimal | NCG Increase in energy
26800 | 337.88 | 114.695 | 1190.18 | 309.14 | 1 | 31896824 | 7200 | 229657132800 |  | 222535.9814 | 0.83 | 4.62 | 1238694.2579 | 0.05 | 61934.7129
26800 | 337.88 | 114.695 | 1190.18 | 309.14 | 0.95 | 30716230.4 | 7200 | 221156858880 | 8500273920

## Liq eff savings
BTU difference | natural gas volume (mcf) | Boiler efficiency (decimal) | Gas price / mcf | Gas bill $
8500273920 | 8236.6995 | 0.83 | 4.62 | 45847.6528

## Enthalpy
Dryer Efficiency Spreadheet
Convective Dryers
| Pressure | 1010 | hPa | [11 empty] | AH Normalized |  | Hum ratio | grams water /g dry air | specific humidity | grams water/kg moist air
| Temperature C -Ambient | 18.6 | C | 0.99943 | Cv | 21.4652 | Ps | 15.951 | g/m3 sat
| Relative Humidity | 40 | %RH | 6.3804 | g/m3 | 8.5861 | Pd | 0.85113 | %vol | 0.0053328 | kg/kg | 4.7642 | DP | 6.8149 | g/m3 corrected to 0 | 6.8352 | g/Nm3 | 5.3328 | g/kg | 842.0924 | g/kg
| Mass flow rate | 55431 | kg/hr
| Humidity ratio - inlet | 0.0053328
| Dry gas density | 1.2059 | kg/m3
| Mol wt mixed gas | 28.8676 | kg/kmol
| Mixed gas density | 1.202 | kg/m3
| Gas flow rate | 60171 | m3/hr
| Temperature -Inlet | 179 | C
| Temperature -Outlet | 85 | C | 76.208 | Pd | 577.3189 | Ps
| Enthalpy - Ambient | 32.229 | kJ/kg
| Enthalpy - Inlet | 195.1482 | kJ/kg
| Enthalpy - Outlet | 210.1482 | kJ/kg
| Energy Usage | 9030774.1029 | kJ/hr
| H2O mass (solids) - IN | 2359 | kg/hr
| H2O mass (solids) - Out | 53 | kg/hr
| Evaporation rate | 2306 | kg/hr
| Evaporation Energy - min | 5303800 | kJ/hr
| Humidity ratio - outlet | 0.046934
| Dryer efficiency | 0.5873
| Exhaust RH | 13.2003
Molecular Wt of Water= | 18.106 | kg/kmol
Molecular Wt of air= | 28.96 | kg/kmol
Universal Gas Constant | 8.314 | J/kmol
Gas Constant of Air= | 0.28709 | kJ/(kg K)
Gas Constant of Water= | 0.45918 | kJ/(kg K)
Evaporation constant | 2300 | kJ/kg
Specific heat of air, Cp | 1.006 | kJ/(kg K)

## Feed water temp control
FW temp drop (F) | BTU Deviation (Btu/kWh) | Turbine System efficiency (decimal) | Gas price / mmbtu | Plant capacity | hours per year | Plant capacity (MW) | Fuel savings
15 | 6 | 0.75 | 3 | 0.8 | 8760 | 300 | 50457.6