## Acid Dewpoint Calculator
Acid Dewpoint Calculator - Natural Gas / HRSG Exhaust
Input / Output | Value | Units | Description | Formula / Notes | Customer Case 1 | Customer Case 2 | Customer Case 3
Exhaust moisture | 15 | vol % | Real-time stack/exhaust gas moisture sensor value | Input | 8 | 10 | 12
Natural gas sulfur content | 0.5 | ppmv as S | Sulfur content in natural gas, expressed as ppmv sulfur | Input | 0.1 | 0.25 | 0.5
SO2 to SO3 conversion | 1 | % | Assumed SO2 converted to SO3 through turbine/duct/SCR/catalyst path | Input | 0.5 | 1 | 2
Total pressure | 1 | atm | Use near 1.0 atm for HRSG stack unless corrected | Input | 1 | 1 | 1
Safety margin above ADP | 25 | °F | Minimum stack/cold-end metal margin above acid dewpoint | Input | 25 | 25 | 25
OEM minimum stack temperature | 160 | °F | Site/OEM minimum stack temperature limit | Input | 160 | 160 | 160
Current stack outlet temperature | 205 | °F | Actual/expected HRSG stack outlet temperature before reduction | Input | 205 | 205 | 205
Desired stack outlet temperature | 190 | °F | Candidate target stack outlet temperature after optimization | Input | 190 | 185 | 180
H2O partial pressure | 0.15 | atm | Calculated from exhaust moisture and pressure | 0.15 | 0.08 | 0.1 | 0.12
SO3 concentration | 0.005 | ppmv | Assumes sulfur ppmv as S first oxidizes to SO2; SO3 = sulfur ppmv × conversion fraction | 0.005 | 0.0005 | 0.0025 | 0.01
SO3 partial pressure | 5e-09 | atm | Calculated from SO3 ppmv and pressure | 5e-09 | 5e-10 | 2.5e-09 | 1e-08
Acid dewpoint | 173.8873 | °F | Acid dewpoint calculated by Verhoff-Banchero; T result is Kelvin, then converted to °F | VB formula uses partial pressures in mmHg/Torr; sheet converts atm × 760. Formula: T_F=(T_K-273.15)*9/5+32 | 131.047 | 155.6607 | 177.5319
Minimum controlled stack temperature | 198.8873 | °F | Higher of acid dewpoint + margin and OEM minimum | 198.8873 | 160 | 180.6607 | 202.5319
Available temperature drop | 6.1127 | °F | Current stack outlet temperature less minimum controlled stack temperature; cannot be negative | 6.1127 | 45 | 24.3393 | 2.4681
Desired drop allowed? | No | Yes/No | Checks if desired stack outlet temperature stays above ADP margin / OEM minimum | No | Yes | Yes | No
Allowable final stack temperature | 198.8873 | °F | Highest of desired target and minimum controlled stack temperature | 198.8873 | 190 | 185 | 202.5319
Allowed temperature drop to enter savings sheet | 6.1127 | °F | Current stack temperature less allowable final stack temperature | 6.1127 | 15 | 20 | 2.4681
Notes: Verhoff-Banchero returns absolute temperature in Kelvin and requires H2O/SO3 partial pressures in mmHg/Torr. This sheet converts stack partial pressures from atm to mmHg and then converts K to °F. Validate with OEM/site chemistry and materials limits; protect coldest tube metal temperature, not stack gas temperature alone.
Source / Reference | URL
Verhoff-Banchero acid dewpoint form, commonly cited in engineering literature | https://doi.org/10.1021/ie50527a030
General cold-end corrosion context | https://www.watertechnologies.com/handbook/chapter-22-cold-end-deposition-and-corrosion-control

## Fuel Savings Calculator
Fuel Dollar Savings from HRSG Stack Temperature Reduction
Input | Value | Units | Description | Quick Sensitivity
CC load size | 500 | MW | Current/load basis for combined-cycle block | Temp Drop °F | ΔHR Btu/kWh | Savings $/hr
Desired / available outlet temperature drop | 6.1127 | °F | Linked by default from Acid Dewpoint Calculator allowed drop; override with manual value if desired | 1 | 1.3402 | 2.1778
Current net plant heat rate | 6700 | Btu/kWh | Baseline net heat rate at current load | 2 | 2.6804 | 4.3556
Natural gas price | 3.25 | $/MMBtu | Delivered gas price, not just Henry Hub, for plant economics | 3 | 4.0206 | 6.5335
Exhaust flow basis per MW | 10500 | lb/hr per MW | Default scales from 10.5 MMlb/hr at 1000 MW | 4 | 5.3608 | 8.7113
Exhaust gas Cp | 0.26 | Btu/lb-°F | Specific heat of GT exhaust gas mixture | 5 | 6.701 | 10.8891
Incremental steam cycle efficiency | 25 | % | Fraction of additional recovered stack heat converted to net MW | 10 | 13.402 | 21.7782
Operating hours | 8760 | hr/yr | Annual operating hours for annualized savings | 15 | 20.1029 | 32.6673
|  |  |  | 20 | 26.8039 | 43.5564
Calculated Output | Value | Units | Formula
Estimated exhaust mass flow | 5250000 | lb/hr | =Load MW x exhaust flow per MW
Recovered heat from stack reduction | 8.3438 | MMBtu/hr | =m_exh x Cp x DeltaT / 1,000,000
Incremental net MW from recovered heat | 0.61136 | MW | =Recovered heat x efficiency / 3.412
Heat-rate improvement | 8.1922 | Btu/kWh | =HR_base x DeltaMW / Load MW
New estimated net heat rate | 6691.8078 | Btu/kWh | =HR_base - DeltaHR
Equivalent fuel reduction | 4.0961 | MMBtu/hr | =Load MW x 1000 x DeltaHR / 1,000,000
Fuel savings | 13.3123 | $/hr | =Fuel reduction x gas price
Annual fuel savings | 116615.6647 | $/yr | =Hourly savings x operating hours
Notes: This model assumes the stack temperature drop is achieved by additional useful HRSG heat recovery and scales exhaust flow with CC load. For a plant-specific model, replace exhaust flow per MW with measured GT exhaust flow.
Source / Reference | URL
Energy conversion basis: 1 kWh = 3412 Btu; 1 MMBtu/hr = 0.293 MW thermal | https://www.eia.gov/energyexplained/units-and-calculators/british-thermal-units.php